|  |
| --- |
| MPPT SUNRISE SPECIFICATIONS |
|  | **MPPT****12V-10A-LiFePO4-booST** | **MPPT****24V-10A-LiFePO4-booST** | **MPPT****36V-10A-LiFePO4-booST** | **MPPT****48V-10A-LiFePO4-booST** |
| Topology | Boost | Boost | Boost | Boost |
| Rated Panel (Input) Current | 10 A | 10 A | 10 A | 10 A |
| Minimum Panel Voltage for Charging: | 5 V | 5 V | 5 V | 5 V |
| Maximum Input Panel Voltage | 65 V | 65 V | 65 V | 65 V |
| Maximum Recommended Panel Vmp | 13 V | 26 V | 37 V | 50 V |
| Max Solar Panel Power | 130 W | 260 W | 370 W | 500 W |
| Rated Battery Voltage | 12 V | 28 V | 36 V | 48 V |
| CV Voltage | 15.2 V | 30.4 V | 41.8 V | 57 V |
| Charge Profile: | CC/CV* Medium Cell Voltage
* Max Cell Voltage from BMS by CAN BUS
 |  |
| Peak efficiency | 98% Typ. |  |
| MPP Tracking Efficiency | > 99% (Perturb and Observe) |  |
| MPPT Tracking Speed | 100 ms |  |
| Operating Temperature | -40°C to 85°C |  |
| Self consumption | < 1 W |  |
| Type of power supply | * 12V (isolated DC\DC inside) (Optional)
* Solar panel (Voc\_max 65V)
* Battery (Default)
 |
| Port I/O |
| Data Communication Port | * First CAN-bus Default not isolated, isolated available (Optional) ISO 11898-1 (1Mb max adjustable)
* Second CAN-bus Optional (available isolated or not) ISO 11898-1 (1Mb max adjustable) for gate way node function
 |
| Analog Input Signal\* | * Power supply +5V (max 20mA for channel)
* 2 Channel (Temperature, Current, etc)
 |  |
| Digital Input Signal\* | 2 Channel active low (internal pull up resistance) |  |
| General Purpose Relay Contacts\* | * NC (max 10A, 30V resistive load)
* NO (max 10A, 30V resistive load)
 |  |
| Protection |
| Battery Fuse | 20 A |  |
| Polarity inversion | Y |  |
| Over Temperature | Y (Adjustable) |  |
| Overload | Y (Adjustable) |  |
| Enclosure |
| Environmental Protection | * IP 22
* IP 65 (Optional)
 |  |
| Dimensions (h x w x d) | 146 x 96 x 38 mm (IP22)148 x 94 x 34 mm (IP65) |  |
| Weight | 300 g |  |
| \* configurable for customer necessity |  |